## LAB10
|  |  |  | DATA SHEET |  |  |  | DS No. |  | KSF-9-250
[8 empty] | Rev. |  | 0
[8 empty] | Date |  | 2014-02-04
|  |  |  | KSF BASKET STRAINERS |  |  |  | Prepared |  | MR
[8 empty] | Approved |  | AM
[8 empty] | Project | Krone Filter Solutions GmbH
[8 empty] | Pages |  | 1 de / of 1
GENERAL
1 | Identification (KKS) | [5 empty] | Size of body |  | 9
2 | Nominal Diameter |  |  | DN250 |  |  | Rating |  | 10 bar
3 | KKS (line) | [5 empty] | DN |  | 250
4 | Design codes |  |  | ADW2000-Merkblatt / PED 97/23/EC
5 | Model identification |  |  | KSF
6 | Fluid filtered
7 | Service
TYPE OF CONNECTIONS
8 |  |  |  | DN | Rating
9 | INLET |  |  | 250 | PN10
10 | OUTLET |  |  | 250 | PN10
11 | Drain |  |  | 3/8" | N/A
12 | Vent |  |  | 1/4" | N/A
13 | Differential pressure |  |  | 1/4" | N/A
OPERATNG AND DESIGN PARAMETERS
14 | DESIGN CONDITIONS |  |  |  |  | OPERATING CONDITIONS
15 | Pressure |  |  | 6/10 | bar (clamp/bolt) | Pressure |  |  |  | bar g
16 | Temperature |  |  | (-10) - (+200*) | ºC | Temperature |  |  |  | ºC
17 | Flow |  |  | 440 | m³/h | Flow |  |  |  | kg/h
18 | Pressure drop |  |  |  |  | Pressure drop
19 | DP clean filter |  |  | 0.05 | bar ( ≥100µm) | DP clean filter |  |  | 0.05 | bar ( ≥100µm)
20 | DP dirty filter |  |  | 2 bar (basket design pressure) |  | DP dirty filter |  |  |  | bar
21 | Noise level |  |  | N/A - no source | of noise | Noise level |  |  | N/A - no source | of noise
DESCRIPTIVE CHARACTERISTICS
22 | LOCATION OF EQUIPMENT
23 | FILTER ELEMENT
24 |  | Type |  |  | Basket
25 |  | Basket area |  |  | 3590 cm²
26 |  | Grade of filtration |  |  | 20-10000µm
27 | MATERIALS
28 |  | Body |  |  | EN-GJS-500-7 / GGG-50 / BS 500-7 / ASTM 536 80-55-06 / JIS FCD 500-7
29 |  | Cover |  |  | EN-GJS-500-7 / GGG-50 / BS 500-7 / ASTM 536 80-55-06 / JIS FCD 500-7
30 |  | Gasket |  |  | NBR*
31 |  | Vent & Drain plug |  |  | SS316ti
32 |  | Studs |  |  | Steel, galvanized
33 |  | Nuts |  |  | Steel, galvanized
34 |  | Screen |  |  | SS316
35 |  | Perforated plate |  |  | SS316
ACCESSORIES
36 | Pressure drop indicator
37 | Magnetic filter insert
TESTS AND NON DESTRUCTIVE EXAMINATIONS
38 |  |  |  | SCOPE |  |  |  | APPICABLE RULE
39 | Hydrostatic Test | [6 empty] | AD2000-Merkblatt / PED 97/23/EC
40 | Visual inspection |  |  |  | 100 | %
41 | CE- Declaration of Conformity |  |  |  |  | Operating data is necessary ! |  | PED/97/23/EC
42 | Others
43
44 | Information | [6 empty] | Foundry certified by LR / Lloyds
COATING
45 | INTERNAL |  | Anti-corrosion primer
46 | EXTERNAL |  | Epoxy paint RAL 5010 blue
DIMENSIONS AND WEIGHT
47 | [7 empty] | Dimensions
48 | [7 empty] | A | 599 | mm
49 | [7 empty] | B | 604 | mm
50 | [7 empty] | C | 925 | mm
51 | [7 empty] | D | N/A | mm
52 | [7 empty] | E | 23 | mm
53 | [7 empty] | F | 460 | mm
54 | [7 empty] | Weight | 195 | kg
REMARKS
55 | * Standard is NBR with a range of temperature from (-10) - (+100) ºC; FKM with (-10) - (+200)ºC on request.
56
57
58
59
60 | 02/2014 © by Krone Filter Solutions GmbH, subject to change